## Slide 1
Presented by: Bill Diver

## Slide 2
Three Components of Fuel Maintenance
Sampling and Testing
Chemical Treatments
Mechanical Remediation
Are you Fuel Ready?

## Slide 3: Diesel Contamination – Why?
Ongoing fuel quality management is essential to ensure operations aren’t impacted by contamination.
Why Contamination Occurs
Effects of Contamination
Best Practices: Remediation & Prevention

## Slide 4: Why Contamination Occurs?
Quality of Crude
Advanced Refining Process
Government Regulation: Advent of ULSD
Water Intrusion
Introduction of Bio-Diesel

## Slide 5: Why Contamination Occurs - Quality of Crude
Crude Quality

## Slide 6
Strict specifications and goal to produce as much fuel at lowest cost creates unstable fuel
Mostly distillation < 2006
More catalysts introduced after 2006
  Hydrocracking / hydrodesulfurization
Why Contamination Occurs – Advanced Refining Process

## Slide 7
2006 EPA Clean Air Act: Required sulfur in diesel fuel to be reduced to from 5000ppm to15ppm.
Contamination Occurs - ULSD
Hydrodesulfurization removes chemistry essential to preventing microorganism growth.

## Slide 8
Low sulfur and unstable fuel creates environment for microbial contamination and quick degradation
Microbes degrade fuel quality, advance tank and advance corrosion
Not a new issue, but a new problem
Why Contamination Occurs – Water Intrusion

## Slide 9
More Water in Fuel from the Refinery
Condensation Formed on Tank Walls
Tank Vents, Expose Fuel to Humidity & Water Absorption
Water from Fuel Distributor Tanker
Spill Buckets Full of Water
Water Intrusion – How?

## Slide 10
Most common biodiesel concentrations are B2, B5, & B20
Biodiesel has a higher lubricity rating than straight diesel but contains less energy
Biodiesel has one-fourth the shelf life than straight diesel has, and it is more susceptible to microbial growth
Biodiesel tends to gel at higher temperatures than straight diesel
Biodiesel chemistry bonds easily with water
Why Contamination Occurs – Introduction of Biodiesel

## Slide 11
Diesel Contamination in Generators - Effects
Ongoing fuel quality management is essential to ensuring operations aren’t impacted by contamination
Why Contamination Occurs
Effects of Contamination
Best Practices: Remediation & Prevention

## Slide 12
Fuel Filter Plugging
Combustion Chamber Deposits
Lacquering of Injection System Components & Valves
Excessive Soot Accumulation in DP Filters
Reduced Engine Power
Greater Engine Wear due to Particulate
Reduced Fuel Economy
Diesel Contamination - Effects on Engines
Critical System Power Failure
Related to Poor Fuel Quality
80%

## Slide 13
Sub-base Fuel Tank
(Interior Construction Features)
Limited Access
Diesel Contamination - Effects
Low Fuel Turnover

## Slide 14
Examples of what we see in the field…
Why Contamination Occurs – Water Intrusion

## Slide 16
Plugged fuel filter caused by
bio-mass & microbe excreted waste
Asphaltenes removed from tank bottoms developed due to unstable fuel
Diesel Contamination - Effects

## Slide 17
Microbes can come from the air, moisture or during tank filling
Biomass: Microbes can multiply from one cell to 246,000 in six hours
Diesel Contamination - Effects

## Slide 18
Bacteria excrete acids that can corrode metal parts
Fuel tanks, pipes, injectors, injector pumps & fuel lines can be severely damaged
Diesel Contamination - Effects

## Slide 19
1. In-field Sampling & Testing
2. Chemical Treatment
3. Mechanical Tank Cleaning & Fuel Filtration
Three Components of Managing Fuel Quality
Diesel Contamination – Best Practices

## Slide 20
Sampling & Testing
Diesel Contamination – Best Practices
Notes: DAN -

## Slide 21
Sampling practices
ASTM D4057 vs. D7464
Bottom and 3-phase samples
Proper handling of instruments
Sterilization between samples
Temperature Control
Time Sensitive Testing
Condition Monitoring & Sampling - Mythologies
Notes: Dan -

## Slide 22: Suggested “Mission Critical” Testing Criteria
Testing Consists Of…
  D86 Distillation
  D93 Flash Point
  D130 Copper Strip Corrosion
  D287/D4052 API Gravity
  D976 Cetane Index
  D2709 Water & Sediment
  D6304/D7546 Water by Karl Fischer
  D2622/D5453/D7035 Sulfur Content
Notes: Dan -

## Slide 23
Other Testing Methods
Notes: Dan -

## Slide 24
Chemical Solutions
Notes: Bill one of the three components of fuel maintenance Chemical application

## Slide 25: Bellicide Biocide
Choosing the right biocide is important. Solving bacteria and fungus problems is serious business. It’s important to make the right decision.

## Slide 26: DFS Plus and Demulsified EB Water Control Chemistry

## Slide 27
Bell SDF
Sludge Dispersant
Sludge dispersants are an important tool for the health of your stored fuels.

## Slide 28: Dee Zol Life & Bio Dee-Zol Life Stabilizer
Fuel stabilizers are essential for stored fuel health. When it comes to stability improvers for diesel fuels, there are lots of options to consider.
Notes: Bill

## Slide 29: Additional Chemical Solutions
Cold Flow Improver
Super - Tane
Dee-Zol
Bio Dee Zol
Ethanol Defense
Notes: Bill

## Slide 30
Mechanical Remediation
Sweep / Chemically Treat / Aerate
Full Filtration
Phase Separation
Notes: Bill

## Slide 31
Real World Examples
Sweep Treat Aerate
Notes: James

## Slide 32
Real World Examples
Full Filtration
Notes: James

## Slide 33
Real World Examples
Phase Separation
Notes: James

## Slide 34
Thank You For Your Time
Questions?
Bill Diver
Email: bdiver@bellperformance.net
Phone: 407-831-5021